## Sheet1
Name	Code	Unit	Category	Description
Elect_Identifier	0-0:96.1.1.255		Electricity	Equipment identifier
Elect_Delivered_Low_1	1-0:1.8.1.255	kWh		Meter Reading electricity delivered to client (low tariff) in 0,001 kWh
Elect_Delivered_Normal_1	1-0:1.8.2.255	kWh		Meter Reading electricity delivered to client (normal tariff) in 0,001 kWh
Elect_Delivered_Low_2	1-0:1.8.2.255	kWh		Meter Reading electricity delivered by client (low tariff) in 0,001 kWh
Elect_Delivered_Normal_2	1-0:2.8.1.255	kWh		Meter Reading electricity delivered by client (normal tariff) in 0,001 kWh
Tariff_Indicator	1-0:2.8.2.255			Tariff indicator electricity. The tariff indicator can be used to switch tariff
Dependent_Loads	0-0:96.14.0.255			dependent loads e.g boilers. This is responsibility of the P1 user
Actual_Deliverd	1-0:1.7.0.255	kW		Actual electricity power delivered (+P) in 1 Watt resolution
Actual_Received	1-0:2.7.0.255	kW		Actual electricity power received (-P) in 1 Watt resolution
Power_Failures	0-0:96.7.21.255			Number of power failures in any phases
Power_Failures_Long	0-0:96.7. 9.255			Number of long power failures in any phases
Power_Failure_log	1-0:99:97.0.255			Power failure event log
L1_Voltage_Sags	1-0:32.32.0.255			Number of voltage sags in phase L1
L2_Voltage_Sags	1-0:52.32.0.255			Number of voltage sags in phase L2
L3_Voltage_Sags	1-0:72.32.0.255			Number of voltage sags in phase L3
L1_Voltage_Swells	1-0:32.36.0.255			Number of voltage swells in phase L1
L2_Voltage_Swells	1-0:52.36.0.255			Number of voltage swells in phase L2
L3_Voltage_Swells	1-0:72.36.0.255			Number of voltage swells in phase L3
L1_Voltage	1-0:32.7.0.255	V		Instantaneous voltage L1
L2_Voltage	1-0:52.7.0.255	V		Instantaneous voltage L2
L3_Voltage	1-0:72.7.0.255	V		Instantaneous voltage L3
L1_Current	1-0:31.7.0.255	A		Instantaneous current L1
L2_Current	1-0:51.7.0.255	A		Instantaneous current L2
L3_Current	1-0:71.7.0.255	A		Instantaneous current L3
L1_Power+P	1-0:21.7.0.255	kW		Instantaneous active power L1 (+P)
L2_Power+P	1-0:41.7.0.255	kW		Instantaneous active power L2 (+P)
L3_Power+P	1-0:61.7.0.255	kW		Instantaneous active power L3 (+P)
L1_Power-P	1-0:22.7.0.255	kW		Instantaneous active power L1 (-P)
L2_Power-P	1-0:42.7.0.255	kW		Instantaneous active power L2 (-P)
L3_Power-P	1-0:62.7.0.255	kW		Instantaneous active power L3 (-P)
Message	0-0:96.13.0.255			Text message max 1024 characters
Gas_Device_Type_n	0-n:24.1.0.255			Device-Type For Channel n, n in [1, 2, 3, 4]
Gas_Identifier_n	0-n:96.1.0.255			Equipment identifier For Channel n, n in [1, 2, 3, 4]
Gas_Delivered_n	0-n:24.2.1.255	m3		Last 5-minute value (temperature converted) For Channel n, n in [1, 2, 3, 4], gas delivered to client in m3, including decimal values and capture time
Thermal_Device_Type_n	0-n:24.1.0.255			Device-Type For Channel n, n in [1, 2, 3, 4]
Thermal_Identifier_n	0-n:96.1.0.255			Equipment identifier For Channel n, n in [1, 2, 3, 4]
Thermal_Reading_n	0-n:24.1.0.255	GJ		Last 5-minute Meter reading Heat or Cold in 0,01 GJ and capture time For Channel n, n in [1, 2, 3, 4]
Water_Device_Type_n	0-n:24.1.0.255			Device-Type For Channel n, n in [1, 2, 3, 4]
Water_Identifier_n	0-n:96.1.0.255			Equipment identifier For Channel n, n in [1, 2, 3, 4]
Water_Delivered_n	0-n:24.2.1.255			Last 5-minute Meter reading in 0,001 m3 and capture time For Channel n, n in [1, 2, 3, 4]
Mbus_Device_Type_n	0-n:24.1.0.255			Device-Type For Channel n, n in [1, 2, 3, 4]
Mbus_Identifier_n	0-n:96.1.0.255			Equipment identifier For Channel n, n in [1, 2, 3, 4]
Mbus_Delivered_n	0-n:24.2.1.255			Last 5-minute Meter reading and capture time For Channel n, n in [1, 2, 3, 4]